Request for Quotation (RFQ) – Goods & Services

Supply, testing, delivery and unloading of Pipes and Fittings to Warehouses of Multiple Cities Local Water and Sanitation Corporation/Authority - Yemen.

Lot 3:  Supply, testing, delivery and unloading of HDPE Pipes, DI Pipes, GI pipes and fittings to LWSCs- Warehouses of - Local Water and Sanitation Corporations/Authorities - Taiz (Al - Turbah) - Yemen

Section III: Returnable Bidding Forms

The following returnable forms are part of this RFQ and must be completed and returned by bidders as part of their Quotation.

This Section comprises the following Returnable Bidding Forms:

- Form A: Quotation Submission Form

- Form B- Price Schedule Form

- Form C: Technical Quotation Form

- Form D: Previous Experience Form

- Form E: Bidder Information Form

- Form F: Joint Venture Partner Information Form

- FORM H: United Nations Supplier Code Of Conduct Declaration

Form A: Quotation submission form

Bidders are requested to complete this form, sign it and return it as part of their bid submission. The bidder shall fill in this form in accordance with the instructions indicated. No alterations to its format shall be permitted and no substitutions shall be accepted.

Date: [Insert submission date]

Subject: Quotation for ……………………………………………………   RFQ Case No. RFQ/2026/xxxx, dated [insert date]

We, the undersigned, declare that:

  - We offer to supply in conformity with the bidding documents, including the UNOPS General Conditions of Contract;

  - Our quotation shall be valid for the period of time of [insert number of days which shall not be less than the specified in Section I: RFQ Particulars, Period of Validity of Quotations] from the date fixed for the submission deadline as set out in the RFQ, and it shall remain binding upon us and may be accepted at any time before the expiration of that period;

  - We have no conflict of interest in any activity that would put it, if selected for this assignment, in a conflict of interest with UNOPS. [If you have any actual or potential conflict of interest as defined in Article 3 of Section II: Instructions to Bidders, please disclose it here];

  - Our firm confirms that the offeror and sub-contractors have not been associated, or had been involved in any way, directly or indirectly, with the preparation of the design, terms of references and/or other documents used as a part of this solicitation;

  - Our firm, its affiliates or subsidiaries—including any subcontractors or suppliers for any part of the Contract—has not been declared ineligible by UNOPS, nor is included in the suspended/ineligibility list of the UN/PD, other UN Agencies, the UN Security Council, and the World Bank, in accordance with Instructions to Bidders Article 3, Eligibility;

  - We embrace the UN Supplier Code of Conduct and adhere to the principles of the UN Global Compact;

  - We have not declared bankruptcy, are not involved in bankruptcy or receivership proceedings, and there is no judgment or pending legal action against them that could impair their operations in the foreseeable future;

  - We have not offered and will not offer fees, gifts and/or favours of kind in exchange for this RFQ and will not engage in any such activity during the performance of any Contract awarded.

I, the undersigned, certify that I am duly authorized by [insert full name of bidder] to sign this quotation and bind [insert full name of bidder] should UNOPS accept this quotation:

Name: [complete]

Title: [complete]

Date: [complete]

Signature: _____________________________________________________________

Provide the name and contact information for the primary contact from your company for this quotation:

Name: [complete]

Title: [complete]

Email address: [complete]

Telephone: [complete]

Form B: Price Schedule Form

RFQ reference no: RFQ/2026/ XXXX

| Currency | USD |
| --- | --- |

Note: Bidders are required to complete both versions of Form B: the Excel format and the standard document format.

| Lot 3: Supply, testing, delivery and unloading of HDPE Pipes, DI Pipes, GI pipes and fittings to LWSCs- Warehouses of - Local Water and Sanitation Corporations/Authorities - Taiz (Al - Turbah) - Yemen |  |  |  |
| --- | --- | --- | --- |
| Part | Subproject | Description | Pirce In USD |
| 1 | EHC-AF3-WS-TAZ-024-01 | Supply of HDPE Pipes and Fittings | Taiz (Al-Turbah) |
| 2 | EHC-AF3-WS-TAZ-024-02 | Supply of DI Pipes and Fittings | Taiz (Al-Turbah) |
| 3 | EHC-AF3-WS-TAZ-024-03 | Supply of Medium Class GI Pipes and Fittings | Taiz (Al-Turbah) |
| 4 | EHC-AF3-WS-TAZ-024-04 | Supply of Repair Clamps | Taiz (Al-Turbah) |
| 5 | EHC-AF3-WS-TAZ-024-05 | Supply of Valves | Taiz (Al-Turbah) |
| Total Overall Price for Lot# 3 DAP – USD |  |  |  |

Payment terms 30 days accepted: ☐ Yes

Bidder’s discount for accelerated payment: ____% of total firm price for each calendar day less than thirty (30) days List of subcontractors or suppliers

Bidder must identify the names of all subcontractors/suppliers who will be providing good/services under this Contract and the type of work being subcontracted, if applicable.

- _[Full legal name and address of subcontractors]

- _________________________________________________

- ________________________________________________

I, the undersigned, certify that I am duly authorized by [insert full name of Bidder] to sign this quotation and bind [insert full name of Bidder] should UNOPS accept this quotation:

Name	: _____________________________________________________________

Title	: _____________________________________________________________

Date	: _____________________________________________________________

Signature	: _____________________________________________________________

Form C: Technical Quotation Form

RFQ reference no: [insert RFQ reference No.]

Name of Bidder: [insert name of Bidder]

Bidders are required to complete the Comparative Data Tables included in Section III: Schedule of Requirements to demonstrate compliance with UNOPS requirements and insert them below.

Bidders are NOT allowed to make any change in the “UNOPS requirements” columns of the Comparative Data Tables. Such changes might disqualify your quotation.

Technical specifications for Goods and Comparative Data Table

Part 1 - EHC-AF3-WS-TAZ-024-01 - Supply of HDPE Pipes and Fittings

| ITEM#1: HDPE Pipes: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1. 1 | Date of manufacture: New (2025) |  | ☐ Yes ☐ No |  |
| 1. 2 | Manufacturer/Brand |  | To be inserted by bidder |  |
| 1. 3 | Country of origin: |  | To be inserted by bidder |  |
| 1. 4 | Pressure Rating: | SDR 11 (PN16) | ☐ Yes ☐ No |  |
| 1.4.1 | Diameter Range | DN 25 mm – DN 110 mm, please refer additional Techn. Requirement | ☐ Yes ☐ No |  |
| 1. 5 | HDPE pressure Pipes | -100% virgin (with no recycled compound) PE. 100 | ☐ Yes ☐ No |  |  |
|  |  | -MRS ≥ 10 MPa |  |  |  |
|  |  | -Density 0.95–0.965 g/cm³ |  |  |  |
|  |  | -Physical Properties: Melt flow index 0.4–0.55 g/10min; tensile ≥ 25 N/mm²; elongation ≥ 600%; modulus 1200 N/mm² |  |  |  |
| 1. 6 | The standards for PE Pipes shall be Comply with current international standards or equivalents: |  | ☐ Yes ☐ No |  |  |
|  | ● DIN EN ISO 178 |  |  |  |  |
|  | ● DIN EN ISO 527-2 |  |  |  |  |
|  | ● DIN 7728-1 |  |  |  |  |
|  | ● DIN 8074 / ISO 4427 |  |  |  |  |
|  | ● DIN 8075 / ISO 4427 |  |  |  |  |
|  | ● DIN EN ISO 12162 |  |  |  |  |
|  | ● DIN 53752 |  |  |  |  |
|  | ● EN 12201 |  |  |  |  |
| 1. 7 | ● Use: Municipal and urban water supply and distribution systems. |  | ☐ Yes ☐ No |  |  |
|  | ● Compliance certificates verifying potable water suitability (WRAS, NSF, BS 6920, or equivalent). |  |  |  |  |
| 1. 8 | The bidder confirms that manufacturer quality-control test results and reports, as well as batch-traceability documents, will be provided at the delivery stage. |  | ☐ Yes ☐ No |  |  |
| 1. 9 | Packaging & Supply Format: Pipes with a nominal diameter of DN 110 mm or smaller shall be supplied in coiled form, with a maximum coil length of 100 meters, DN>110 mm straight |  | ☐ Yes ☐ No |  |  |
| 1. 10 | Certifications: Manufacturer shall hold valid ISO 9001, ISO 14001, OHSAS 18001 (or equivalent) certifications. |  | ☐ Yes ☐ No |  |  |
| 1.11 | Marking & traceability per ISO/DIN standards |  | ☐ Yes ☐ No |  |  |
| ITEM # 2: PP Compression Fittings (Couplings, Reducers, Tees, Adaptors, Elbows, End Caps) |  |  |  |  |  |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |  |
| 2. 1 | Date of manufacture | 2025 or newer | To be inserted by bidder |  |  |
| 2. 2 | Manufacturer |  | To be inserted by bidder |  |  |
| 2. 3 | Country of origin |  | To be inserted by bidder |  |  |
| 2. 4 | Pressure Rating: | PN16 (16 bar) | ☐ Yes ☐ No |  |  |
| 2. 5 | Types and SIZES | Please refer additional Techn. Requirement | ☐ Yes ☐ No |  |  |
| 2. 6 | - Material: PP-B (UV stabilized); EPDM seals; POM grip rings; stainless steel reinforcement |  | ☐ Yes ☐ No |  |  |
|  | - Pressure Class: PN16 (PN10 for some end caps) |  |  |  |  |
|  | - Threads BSP in accordance with ISO 7-1 / EN 10226 |  |  |  |  |
|  | - Standards: EN ISO 17885, EN 12201-3, EN 681-1or equivalent |  |  |  |  |
|  | - Potable water suitability certificates |  |  |  |  |
|  | - Marking & batch traceability |  |  |  |  |
| 2. 7 | Pressure Class: PN16 and PN10, please refer additional Techn. Requirement |  | ☐ Yes ☐ No |  |  |
| 2. 8 | - Threads BSP in accordance with ISO 7-1 / EN 10226 |  | ☐ Yes ☐ No |  |  |
| 2. 9 | - Standards: EN ISO 17885, EN 12201-3, EN 681-1 or equivalent |  | ☐ Yes ☐ No |  |  |
| 2. 10 | - Potable water suitability certificates |  | ☐ Yes ☐ No |  |  |
| ITEM # 3: P.P. Mechanical Saddle with reinforcing metal ring: |  |  |  |  |  |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |  |
| 3. 1 | Date of manufacture | 2025 or newer | To be inserted by bidder |  |  |
| 3. 2 | - Manufacturer |  | To be inserted by bidder |  |  |
| 3. 3 | - Country of origin |  | To be inserted by bidder |  |  |
| 3. 4 | - Material: PP body, DI/metal rings, EPDM gasket |  | ☐ Yes ☐ No |  |  |
|  | Pressure: PN10 or PN16 as, please refer additional Techn. Requirement |  |  |  |  |
|  | - Type. Mechanical Saddle with reinforcing metal ring |  |  |  |  |
|  | Sizes: Please refer additional Techn. Requirement |  |  |  |  |
|  | - Standards: EN 12201, ISO 1167 or equivalent |  |  |  |  |
| ITEM # 4: Restraint Couplings & Flange Adaptors |  |  |  |  |  |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |  |
| 4.1 | - Date of manufacture | 2025 or above | ☐ Yes ☐ No |  |  |
| 4.2 | - Manufacturer |  | To be inserted by bidder |  |  |
| 4.3 | - Country of origin |  | To be inserted by bidder |  |  |
| 4.4 | - Standards: EN 12842 or equivalent |  | To be inserted by bidder |  |  |
|  | - Working Pressure:PN16 |  |  |  |  |
|  | - Flange Compatibility: EN1092-2or equivalent |  |  |  |  |
|  | - Angular Deflection: ≥ 1.5° |  |  |  |  |
|  | Sizes: Please refer additional Techn. Requirement |  |  |  |  |
|  | Material: |  |  |  |  |
|  | - End Ring: Ductile Iron, FBE Coated |  |  |  |  |
|  | - Grip Ring: Copper Alloy |  |  |  |  |
|  | - Bolts :316 Stainless Steel with Delta Seal Coating |  |  |  |  |
|  | - Elastomeric Seals: EPDM |  |  |  |  |
|  | - Barrel: Ductile Iron, FBE Coated |  |  |  |  |
| Others |  |  |  |  |  |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |  |
| 1 | Warranty: minimum 1-year against manufacturing defects, leakage, or premature failure from the handover certificate date |  | ☐ Yes ☐ No | Insert details |  |

Part 2 - EHC-AF3-WS-TAZ-024-02 - Supply of DI Pipes and Fittings

| Item No. 1 - Fittings |  |  |  |
| --- | --- | --- | --- |
| Item | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 2.1 | Date of manufacture: New (2025) | To be inserted by bidder |  |
| 2.2 | Manufacturer/Brand | To be inserted by bidder |  |
| 2.3 | Country of origin: | To be inserted by bidder |  |
| 2.4 | Classes: K12 (bends, equal tees, reducers/tapers, blanks); K14 (reducer tees) | ☐ Yes ☐ No |  |
| 2.5 | Connections: All double-flanged PN16 (EN 1092-2, or equivalent); complete with: | ☐ Yes ☐ No |  |  |
|  | - EPDM/NBR gaskets |  |  |  |
|  | - SS 304/316 or galvanized carbon steel bolts/nuts/washers |  |  |  |
| 2.6 | Types and sizes: Please refer to additional tech. requirement | ☐ Yes ☐ No |  |  |
| 2.7 | Material: Ductile iron pipes, spheroidal graphite cast iron (to ASTM A536 or equivalent); suitable for drinking water networks | ☐ Yes ☐ No |  |  |
| 2.8 | Standards: EN 545/ISO 2531 or equivalent | ☐ Yes ☐ No |  |  |
| 2.9 | Internal Lining: Cement mortar lining per ISO 4179 or equivalent, suitable for potable water | ☐ Yes ☐ No |  |  |
| 2.1 | External Coating: Zinc coating with protective finish per EN 545 / ISO 2531or equivalent. | ☐ Yes ☐ No |  |  |
| 2.11 | Testing & Inspection: | ☐ Yes ☐ No |  |  |
|  | - Factory hydrostatic tests |  |  |  |
|  | - Site Dimensional checks, coating/lining verification per EN 545 / ISO 2531 or equivalent. |  |  |  |
|  | - Compliance valid certificates Provided |  |  |  |
| 2.12 | Approvals & Compliance: Potable water compliance (WRAS, DVGW, ACS, KIWA, or equivalent) | ☐ Yes ☐ No |  |  |
| 2.13 | Marking & Traceability: Manufacturer/trademark, DN, class (K9/K12/K14), standard reference, batch/date | ☐ Yes ☐ No |  |  |
|  | Packaging & Delivery: Protective end caps, secure bundling, accessories in labelled containers; stored on timber supports, protected from contamination |  |  |  |
| 2.14 | Warranty: Minimum 12 months from handover certificate date against defects in materials, manufacture, or coatings/linings | ☐ Yes ☐ No |  |  |
| 2.15 | Documentation Requirements are provided: | ☐ Yes ☐ No |  |  |
|  | - Material test reports (chemical, mechanical properties) |  |  |  |
|  | - Hydrostatic test records |  |  |  |
|  | - Coating/lining inspection reports |  |  |  |
|  | - Potable water compliance certificates |  |  |  |

Part 3 - EHC-AF3-WS-TAZ-024-03 - Supply of Medium Class GI Pipes and Fittings

| (Medium Class) GI Pipes and Fittings |  |  |  |
| --- | --- | --- | --- |
| Item | Specifications required | Is quotation compliant? Bidder to complete | Bidder’s Offer specifications Bidder to complete |
| 1. GALVANIZED IRON (GI) PIPES |  |  |  |
| 1.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.2 | Manufacturer/Brand | To be inserted by bidder | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.3 | Country of origin: | To be inserted by bidder | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.4 | Pipes are suitable for cold potable water, for buried or exposed installation. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.5 | GI pipes comply with with BS 1387 or BS EN 10255 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.6 | Galvanizing Comply with BS 729 or ASTM A123 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.7 | Threads comply with with BS 21 / ISO 7-1 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.8 | Pipes manufactured from mild steel, uniform composition, defect-free | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.9 | Hot-dip galvanizing applied internally and externally after fabrication and threading | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.10 | Zinc coating mass ≥ 360 g/m² (Galvanizing test report is provided) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.11 | Galvanized surfaces shall be free from blisters, bare spots, peeling, or flaking. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.12 | Medium Class pipes as per BS 1387 / BS EN 10255 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.13 | Medium Series GI Pipes – Nominal Diameters and Minimum Wall Thickness: 20 mm (¾″) – 2.6 mm; 25 mm (1″) – 3.2 mm; 40 mm (1½″) – 3.2 mm; 50 mm (2″) – 3.6 mm; 80 mm (3″) – 4.0 mm. 100 mm (3″) – 4.5 mm | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.14 | Standard pipe length = 6.0 m | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.15 | Dimensional tolerances comply with 10255 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.16 | Pipes threaded at both ends | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.17 | One GI socket supplied per pipe | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.18 | Pipes suitable for working pressure ≥ 12 bar at at 20°C | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.19 | Pressure testing conducted at ≥ 1.5 × working pressure | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.20 | Pipes shall be permanently marked at intervals ≤ 1.5 m. - Marking shall include: - Manufacturer name - Nominal diameter (DN) - Wall thickness - Pipe class (Heavy) - Applicable standard - Batch number - Date of manufacture | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.21 | Minimum 12 months warranty from the handover certificate date. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2. GALVANIZED IRON (GI) FITTINGS |  |  |  |
| 2.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.2 | Manufacturer/Brand | To be inserted by bidder | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 23 | Country of origin: | To be inserted by bidder | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.4 | Fittings manufactured from malleable cast iron | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.5 | hot-dip galvanized Fittings | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.6 | Fittings shall comply with BS EN 10242 or equivalent. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.7 | All required fitting types and sizes are as per additional technical requirement (please refer to additional technical requirement) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.8 | Fittings pressure rating ≥ pipe pressure rating | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.9 | Galvanizing quality of fittings shall be equal to or better than pipes (manufacturer declaration required). | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.10 | Fittings are fully compatible with Medium Class GI pipes. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.11 | Visual inspection of galvanizing performed (Inspection report will be provided at delivery stage) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.12 | Coating adhesion verified by Preece Test (Test certificate will be provided at delivery stage) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.13 | Manufacturer operates documented QC system (ISO 9001 or equivalent is provided) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.14 | Marking includes manufacturer, DN, standard reference | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.15 | Minimum 12 months warranty from the handover certificate date. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |

Part 4 - EHC-AF3-WS-TAZ-024-04 - Supply of Repair Clamps

| Item No 1 - Stainless Steel Repair Clamp |  |  |  |
| --- | --- | --- | --- |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 1.2 | Manufacturer/Brand | To be inserted by bidder |  |
| 1.3 | Country of origin: | To be inserted by bidder |  |
| 1.4 | Clamp body material: Pre-rolled stainless steel 304L (or 316L for highly corrosive environments), fully welded, pickled, and passivated | ☐ Yes ☐ No |  |
| 1.5 | Clamp design: Integrated hinge point for simplified installation | ☐ Yes ☐ No |  |
| 1.6 | Fasteners: Stainless steel A4 bolts, nuts, washers, anti-galling treated | ☐ Yes ☐ No |  |
| 1.7 | Gasket: Waffle-structured EPDM rubber, vulcanized, rounded tops, fully circumferential | ☐ Yes ☐ No |  |
| 1.8 | Spanner plate: Vulcanized, integrated with gasket to maintain uniform compression | ☐ Yes ☐ No |  |
| 1.9 | Working pressure: - DN 80–150: 16 bar - DN 175–450: 10 bar; - DN 500+: 6 bar | ☐ Yes ☐ No |  |
| 1.1 | Tolerance (double band clamp): Max ±24 mm depending on pipe diameter | ☐ Yes ☐ No |  |
| 1.11 | Temperature range: -20°C to +80°C (standard EPDM) | ☐ Yes ☐ No |  |
| 1.12 | Corrosion resistance: Suitable for potable water | ☐ Yes ☐ No |  |
| 1.13 | Sealing: Fully circumferential with even compression to prevent leakage and minimize pipe stress | ☐ Yes ☐ No |  |
| 1.14 | Standards compliance: ISO 9001 (manufacturing) or equiv | ☐ Yes ☐ No |  |
| 1.15 | Installation: Quick and easy due to hinge design; even torque application ensures uniform gasket compression | ☐ Yes ☐ No |  |
| 1.16 | Warranty: Minimum 1-year against manufacturing defects and leakage | ☐ Yes ☐ No |  |
| 1.17 | Marking: Manufacturer name, material grade, pipe size range, PN rating, and date of manufacture | ☐ Yes ☐ No |  |

Part 5 - EHC-AF3-WS-TAZ-024-05 - Supply of Valves

| Item No 1 . Flanged Soft Sealing Gate Valves |  |  |  |
| --- | --- | --- | --- |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Design standard: EN 1074-1 & 2 | ☐ Yes ☐ No |  |
|  | - Face-to-face: EN 558 Table 2 Basic Series 3 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Flanges: EN1092-2 (ISO 7005-2), PN16 |  |  |
|  | - Body: Ductile Iron GJS-500-7 (GGG-50), FBE coating 250 µm |  |  |
|  | - Bonnet: Ductile Iron GJS-500-7 (GGG-50), FBE coating 250 µm |  |  |
|  | - Wedge core & body: Ductile Iron GJS-500-7 (GGG-50) |  |  |
|  | - Wedge shoe: Polyamide or equivalent |  |  |
|  | - Wedge rubber: EPDM, potable water approved |  |  |
|  | - Wiper ring & O-rings: NBR rubber |  |  |
|  | - Stem: Stainless Steel 316L |  |  |
|  | - Stem nut: Brass DZR CW626N |  |  |
|  | - Thrust collar: Brass DZR CW602N |  |  |
|  | - Stop ring: Stainless steel 316L |  |  |
|  | - Stem seal: EPDM rubber |  |  |
|  | - Bushing: Polyamide or equivalent |  |  |
|  | - Bonnet gasket: EPDM rubber |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304, sufficient for all flange faces |  |  |
| 2 | Brass Threaded Gate Valve |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Design: Female/Female threaded, handle in steel | ☐ Yes ☐ No |  |
|  | - Body material: Brass CW617N or DZR CW602N |  |  |
|  | - Threads: ISO228 (DIN EN ISO 228 / BS EN ISO 228) |  |  |
|  | - Working temperature: 0°C to 90°C (no steam) |  |  |
| 3 | Flanged Check Valve (Swing/Non-return) |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Swing type | ☐ Yes ☐ No |  |
|  | - Standards: EN 558-1 Series 10, BS 5153 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Working temperature: up to 60°C |  |  |
|  | - Body & cover: Ductile Iron GJS-500-7 (GGG50), FBE coating 250 µm |  |  |
|  | - Seat: Bronze |  |  |
|  | - Sealing disc: Ductile Iron GJS-500-7 |  |  |
|  | - Shaft & lever shaft: Stainless Steel 316L or X20Cr13 |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304 |  |  |
| 4 | Flanged Double Orifice Air Relief Valve |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Flanged Double Orifice Air Relief Valve | ☐ Yes ☐ No |  |
|  | - Standard: EN 1074-4/BS 5153 (performance), EN 558-1 (dimensions) |  |  |
|  | - Body & bonnet: Ductile Iron GJS-500-7 (GGG50), FBE coating 250 µm |  |  |
|  | - Guides, orifice, seat, plug: ABS / PP / Polyamide |  |  |
|  | - Sealing ring & gasket: EPDM rubber |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Function: Triple Orifice (vent air during filling, admit air during draining, release entrained air) |  |  |
| 5 | Others for all Valves |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | The manufacturer shall operate under a certified Quality Management System compliant with ISO 9001:2015. | ☐ Yes ☐ No |  |
| 2 | Full material traceability certificates shall be provided upon request. | ☐ Yes ☐ No |  |
| 3 | Approved for contact with drinking water | ☐ Yes ☐ No |  |
| 4 | Valves shall be 100% factory tested to EN standards (shell, seat leakage, functional tests); type test reports for pressure, endurance, and coating will be submitted at delivery stage with all Factory Test Certificates | ☐ Yes ☐ No |  |
| 5 | Each valve shall be permanently and clearly marked with: | ☐ Yes ☐ No |  |
|  | Manufacturer’s name or trademark |  |  |
|  | ● Nominal diameter (DN) |  |  |
|  | ● Pressure rating (PN) |  |  |
|  | ● Material designation |  |  |
|  | ● Direction of flow (where applicable) |  |  |
| 6 | Packaging, Handling, and Transportation: | ☐ Yes ☐ No |  |
|  | Valves shall be individually protected against dust, moisture, and impact, with flange ends covered, and packaged suitably for long-distance transport and storage under harsh climatic conditions. |  |  |
|  | Warranty and Defect Liability: |  |  |
|  | The/supplier shall provide a minimum warranty of 12 months from date of handover certificate, during which any valve defective due to design, material, or manufacturing faults shall be repaired or replaced at no cost to the Purchaser. |  |  |

- Delivery requirements – Comparative Data Table:

| UNOPS Requirements |  | Is quotation compliant? Bidder to complete | Details Bidder to complete |
| --- | --- | --- | --- |
| Delivery time | The Bidder shall deliver the goods within 6 months after the Contract signature. | ☐ Yes ☐ No | Insert details |
| Delivery place and Incoterms rules | Part 1,2,3,4 and 5, DAP as per Incoterms 2020 at Warehouses of National/Local Water & Sanitation Authorities at Taiz (Al - Turbah) - Yemen – Yemen | ☐ Yes ☐ No | Insert details |
| UNOPS Right to vary requirements | At the time the Contract is awarded, UNOPS reserves the right to vary the quantity of the goods and associated services specified above, provided this does not exceed +/- [20%] , without any change in the unit prices or other terms and conditions of the RFQ. | ☐ Yes ☐ No | Insert details |

ANY DEVIATION MUST BE LISTED BELOW:

________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Name	: _____________________________________________________________

Title	: _____________________________________________________________

Date	: _____________________________________________________________

Signature	: _____________________________________________________________

# Form D: Previous experience form

Name of Bidder: [insert name of Bidder]

Previous experience:

Previous experience: The bidder should have successfully completed at least two (2) similar contracts within the last Seven (7) years from the date of the bid opening. At least one of the previous contracts should be a minimum of USD 75,000 USD value.

(Similar means supply of Pipes, Fittings, Clamps, Flanges, Valves or related goods and Equipment’s).

In case of Joint Venture (JV), all joint venture members combined must meet it. Bidder to complete Form D: Previous Experience Form and attached documentary evidence to establish compliance. The requirement is for ALL lots.

| Description of services/goods | Country | Total amount of Contract | Contract Identification and Title and Contact details of Client (Name, Address, telephone, email, fax) | Year project was undertaken |
| --- | --- | --- | --- | --- |

- All current contracts underway

| No. | Contract title | Client | Location | Contract amount | Value of remaining work |
| --- | --- | --- | --- | --- | --- |

- All contracts committed to start

| No. | Contract title | Client | Location | Contract amount | Value of remaining work |
| --- | --- | --- | --- | --- | --- |

Name	: _____________________________________________________________

Title	: _____________________________________________________________

Date	: _____________________________________________________________

Signature	: _____________________________________________________________

Form E: Bidders Information

The Bidder shall fill in this Form in accordance with the instructions indicated below. No alterations to its format shall be permitted and no substitutions shall be accepted.

RFQ reference no: [insert RFQ reference No.]

Name of Bidder: [insert name of bidder]

Date: [insert submission date]

- Background and Expertise of Organization:

| Full legal name of Bidder | [complete] |
| --- | --- |
| What year was your firm/organization established? | [complete] |
| Address of registered office | [complete] |
| Name of bidder Representative | complete] |
| Has your firm/organization ever filed or petitioned for bankruptcy? (If YES, explain in detail the reasons why, filing date, and current status.) | [complete] |
| Does your firm have an actual or potential conflict of interest in this procurement process? (Refer to Section II: Instructions to Bidders, Article 4, for details on conflict of interest) | [Insert either “No”, or “Yes” in which case please provide details on your actual or potential conflict of interest here] |

- UNGM Registration and UNOPS Vendors

As part of the bid, it is desired that the Bidder goes to the United Nations Global Marketplace (UNGM) registration website: https://www.ungm.org/Account/Registration and fills out the registration.

If the Bidder is already registered with UNGM, please provide your UNGM registration number in the table below and please ensure that your firm’s information on UNGM is current.

The Bidder may still bid even if not registered with the UNGM. However, if the Bidder is selected for Contract award, the Bidder must register on the UNGM prior to Contract signature.

| Are you a UNGM registered vendor? | ☐ Yes ☐ No If yes, [insert UGNM vendor number] |
| --- | --- |
| Are you a UNOPS vendor? | ☐ Yes ☐ No |

- Contact details of persons that UNOPS may contact for requests for clarification during bid evaluation:

| Name/Surname | [complete] |
| --- | --- |
| Title | [complete] |
| Tel Number (direct) | [complete] |
| Email address (direct): | [complete] |

Form F: Joint Venture Partner Information Form

[The Offeror shall fill in this Form in accordance with the instructions indicated below]

RFP reference no: [insert RFP reference No.]

Name of Offeror: [insert name of Offeror]

Date: [insert submission date]

To be completed and returned with your Proposal if the Proposal is submitted as a Joint Venture/Consortium/Association.

| JV / Consortium/ Association Information |  |
| --- | --- |
| Name | [complete] |
| Names of each partner and contact information (address, telephone numbers, fax numbers, e-mail address) | [complete] |
| Name of leading partner (with authority to bind the JV, Consortium, Association during the RFP process and, in the event a Contract is awarded, during contract execution) | [complete] |
| Proposed proportion of responsibilities between partners (in %) with indication of the type of the services to be performed by each | [complete] |

Signatures of all partners of the JV:

We hereby confirm that if the contract is awarded, all parties of the Joint Venture/Consortium/Association shall be jointly and severally liable to UNOPS for the fulfillment of the provisions of the Contract.

Name of partner: ________________________		Name of partner: _________________________

Signature: ______________________________		Signature: _______________________________

Date: _______________________				Date: ________________________

FORM H: UNITED NATIONS SUPPLIER CODE OF CONDUCT DECLARATION OF ELIGIBILITY

UNOPS expects all bidders to act in accordance with the highest ethical standards throughout the competitive procurement process, as well as during the validity of any contract that may be awarded to them through the process. Therefore, all bidders must declare and ensure the following.

If the bidder’s status in relation to this declaration changes, it must inform UNOPS immediately. Failure to comply with this requirement shall automatically render the bidder ineligible. This document does not require notarization.

Bid for the [insert date]. RFQ ref . RFQ/2026/, dated [insert date]

The undersigned, on submission of a bid for the competitive procurement process or invitation to bid (hereinafter referred to as “the bid”) for the [insert brief description of the goods and/or services] in [name of country/city] – invitation to bid no.: Invitation to bid no.: [insert invitation to bid ref. no.], in response to the call for bids made by the United Nations Office for Project Services (UNOPS), I hereby make the following statements:

We have not and shall not engage in proscribed practices in connection with the UNOPS competitive procurement processes. For the purposes of this provision, a “proscribed practice” means any of those listed on the UNOPS website under “Vendor Sanctions”, including those listed below:

- Corrupt practice: the offering, giving, receiving, or soliciting, directly or indirectly, of anything of value to influence improperly the actions of another party.

- Fraudulent practice: any act or omission, including a misrepresentation, that knowingly or recklessly misleads, or attempts to mislead, a party to obtain a financial or other benefit or to avoid an obligation.

- Coercive practice: any act or omission that impairs or harms, or threatens to impair or harm, directly or indirectly, any party or the property of the party to improperly influence the actions of a party.

- Collusive practice: an arrangement between two or more parties designed to achieve an improper purpose, including influencing improperly the actions of another party.

- Unethical practice: conduct or behaviour that is contrary to the conflict of interest, gifts and hospitality, post-employment provisions or other published requirements of doing business with UNOPS.

- Obstruction: acts or omissions by a vendor that prevent or hinder UNOPS from investigating instances of possible proscribed practices.

We understand that in the event of any breach of these declarations or guarantees, UNOPS shall have the right to reject any bid submitted by us and may terminate any contract awarded to us as a result of any competitive procurement process, giving immediate notice thereof, and that UNOPS shall not be liable for termination charges or any other charges. In addition, UNOPS may exclude us from future work with the organization or other entities within the United Nations system.

We commit to adhering to the highest ethical standards during the execution of any contract, in accordance with point 40. Ethics and corrupt practices of Section II: instructions to bidders of the bidding document.

We understand that UNOPS may cancel or terminate the contract, without penalty and without notice, if we are found to have engaged in collusion, corrupt practices or unethical behaviour, and may also declare us – both our organization and its board of directors and/or individual staff – ineligible indefinitely or for a limited period of time. We understand that UNOPS may also cancel or rescind contracts for the same reason.

We shall not employ, nor do we plan to employ, any person who has been a United Nations official in the past year. If an employee has been a United Nations official, they shall have had no professional relationship with us in the last three (3) years of their service with the United Nations.

The above statements are also true and complete for the members of the joint venture: YES ☐ NO ☐ [If the answer is NO, details must be included of the members for whom any of the above statements are not met. This paragraph may be deleted if the Bidder is not a joint venture].

Name	: _____________________________________________________________

Position 	: _____________________________________________________________

Date	: _____________________________________________________________

Signature	: _____________________________________