Section II: Schedule of Requirements

Supply, testing, delivery and unloading of Heavey Class GI Pipes, Repair Clamps and valves to LWSCs- Warehouses of - Local Water and Sanitation Corporations/Authorities - Taiz City - Yemen

Lot 2:  Supply, testing, delivery and unloading of Heavey Class GI Pipes, Repair Clamps and valves to LWSCs- Warehouses of - Local Water and Sanitation Corporations/Authorities - Taiz City – Yemen

- Summary of requirements

| Part | Subproject ID | Description | Destination City |
| --- | --- | --- | --- |
| 1 | EHC-AF3-WS-TAZ-018-02 | Supply of Heavy Class GI Pipes and Fittings | Taiz City |
| 2 | EHC-AF3-WS-TAZ-018-03 | Supply of Repair Clamps | Taiz City |
| 3 | EHC-AF3-WS-TAZ-018-04 | Supply of Valves | Taiz City |

## Technical specifications for Goods and Comparative Data Table

Part 1 - EHC-AF3-WS-TAZ-018-02 - Supply of Heavy Class GI Pipes and Fittings

| Item No. 1. GALVANIZED IRON (GI) PIPES |  |  |  |
| --- | --- | --- | --- |
| Item | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 1.2 | Manufacturer/Brand | To be inserted by bidder |  |
| 1.3 | Country of origin: | To be inserted by bidder |  |
| 1.4 | Pipes are suitable for cold potable water, for buried or exposed installation. | ☐ Yes ☐ No |  |
| 1.5 | GI pipes comply with IS 1239 (Part 1) / BS EN 10255 / ASTM A53 or equivalent | ☐ Yes ☐ No |  |
| 1.6 | Compliance with BS 729 or ASTM A123/IS 4736 or equivalent for galvanizing | ☐ Yes ☐ No |  |
| 1.7 | - Threads comply with ISO 228 / BS EN ISO 228 or equivalent | ☐ Yes ☐ No |  |
|  | - Threads are clean, uniform, and damage-free |  |  |
| 1.8 | Pipes manufactured from mild steel, uniform composition, defect-free | ☐ Yes ☐ No |  |
| 1.9 | Hot-dip galvanizing applied internally and externally after fabrication and threading | ☐ Yes ☐ No |  |
| 1.1 | Zinc coating mass ≥ 360 g/m² (Galvanizing test report is provided) | ☐ Yes ☐ No |  |
| 1.11 | Galvanized surfaces shall be free from blisters, bare spots, peeling, or flaking. | ☐ Yes ☐ No |  |
| 1.12 | Heavy Class pipes as per IS 1239 (Part 1) / BS EN 10255 / ASTM A53 or equivalent | ☐ Yes ☐ No |  |
| 1.13 | Heavy Series GI Pipes – Nominal Diameters and Minimum Wall Thickness: | ☐ Yes ☐ No |  |
|  | 15 mm (½″) – 3.2 mm; |  |  |
|  | 20 mm (¾″) – 3.2 mm; |  |  |
|  | 25 mm (1″) – 4.0 mm; |  |  |
|  | 40 mm (1½″) – 4.0 mm; |  |  |
|  | 50 mm (2″) – 4.5 mm; |  |  |
|  | 80 mm (3″) – 5.0 mm. |  |  |
| 1.14 | Standard pipe length = 6.0 m | ☐ Yes ☐ No |  |
| 1.15 | Dimensional tolerances comply with applicable manufacturing standard | ☐ Yes ☐ No |  |
| 1.16 | Pipes threaded at both ends | ☐ Yes ☐ No |  |
| 1.17 | One GI socket supplied per pipe | ☐ Yes ☐ No |  |
| 1.18 | Pipes suitable for working pressure ≥ 25 bar | ☐ Yes ☐ No |  |
| 1.19 | - Pressure testing conducted at ≥ 1.5 × working pressure | ☐ Yes ☐ No |  |
|  | - Hydrostatic test pressure: ≥ 37.5 bar per pipe. |  |  |
| 1.2 | Pipes shall be permanently marked at intervals ≤ 1.5 m. | ☐ Yes ☐ No |  |
|  | ● Marking shall include: |  |  |
|  | ● Manufacturer name |  |  |
|  | ● Nominal diameter (DN) |  |  |
|  | ● Wall thickness |  |  |
|  | ● Pipe class (Heavy) |  |  |
|  | ● Applicable standard |  |  |
|  | ● Batch number |  |  |
|  | ● Date of manufacture |  |  |
| 1.21 | Minimum 12 months warranty from the handover certificate date. | ☐ Yes ☐ No |  |
| 2. GALVANIZED IRON (GI) FITTINGS |  |  |  |
| Item | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 2.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2.2 | Manufacturer/Brand | To be inserted by bidder |  |
| 23 | Country of origin: | To be inserted by bidder |  |
| 2.4 | Fittings manufactured from malleable cast iron | ☐ Yes ☐ No |  |
| 2.5 | hot-dip galvanized Fittings | ☐ Yes ☐ No |  |
| 2.6 | Fittings shall comply with: | ☐ Yes ☐ No |  |
|  | ● BS EN 10242 |  |  |
|  | ● ASTM A197 |  |  |
|  | or equivalent. |  |  |
| 2.7 | All required fitting types and sizes Please refer to additional technical requirement | ☐ Yes ☐ No |  |
| 2.8 | Fittings pressure rating ≥ pipe pressure rating | ☐ Yes ☐ No |  |
| 2.9 | Galvanizing quality of fittings shall be equal to or better than pipes (manufacturer declaration required). | ☐ Yes ☐ No |  |
| 2.1 | -Fittings are fully compatible with Heavy Class GI pipes. | ☐ Yes ☐ No |  |
|  | -Threads comply with ISO 228 / BS EN ISO 228 or equivalent and are clean, uniform, and damage-free. |  |  |
| 2.11 | Visual inspection of galvanizing performed (Inspection report will be provided at delivery stage) | ☐ Yes ☐ No |  |
| 2.12 | Coating adhesion verified by Preece Test (Test certificate will be provided at delivery stage) | ☐ Yes ☐ No |  |
| 2.13 | Manufacturer operates documented QC system (ISO 9001 or equivalent is provided) | ☐ Yes ☐ No |  |
| 2.14 | Marking includes manufacturer, DN, standard reference | ☐ Yes ☐ No |  |
| 2.15 | Minimum 12 months warranty from the handover certificate date. | ☐ Yes ☐ No |  |

Part – 2 - EHC-AF3-WS-TAZ-018-03 - Supply of Repair Clamps

| Item No 1 - Stainless Steel Repair Clamp |  |  |  |
| --- | --- | --- | --- |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 1.2 | Manufacturer/Brand | To be inserted by bidder |  |
| 1.3 | Country of origin: | To be inserted by bidder |  |
| 1.4 | Clamp body material: Pre-rolled stainless steel 304L (or 316L for highly corrosive environments), fully welded, pickled, and passivated | ☐ Yes ☐ No |  |
| 1.5 | Clamp design: Integrated hinge point for simplified installation | ☐ Yes ☐ No |  |
| 1.6 | Fasteners: Stainless steel A4 bolts, nuts, washers, anti-galling treated | ☐ Yes ☐ No |  |
| 1.7 | Gasket: Waffle-structured EPDM rubber, vulcanized, rounded tops, fully circumferential | ☐ Yes ☐ No |  |
| 1.8 | Spanner plate: Vulcanized, integrated with gasket to maintain uniform compression | ☐ Yes ☐ No |  |
| 1.9 | Working pressure: - DN 80–150: 16 bar - DN 175–450: 10 bar; - DN 500+: 6 bar | ☐ Yes ☐ No |  |
| 1.1 | Tolerance (double band clamp): Max ±24 mm depending on pipe diameter | ☐ Yes ☐ No |  |
| 1.11 | Temperature range: -20°C to +80°C (standard EPDM) | ☐ Yes ☐ No |  |
| 1.12 | Corrosion resistance: Suitable for potable water | ☐ Yes ☐ No |  |
| 1.13 | Sealing: Fully circumferential with even compression to prevent leakage and minimize pipe stress | ☐ Yes ☐ No |  |
| 1.14 | Standards compliance: ISO 9001 (manufacturing) or equiv | ☐ Yes ☐ No |  |
| 1.15 | Installation: Quick and easy due to hinge design; even torque application ensures uniform gasket compression | ☐ Yes ☐ No |  |
| 1.16 | Warranty: Minimum 1-year against manufacturing defects and leakage | ☐ Yes ☐ No |  |
| 1.17 | Marking: Manufacturer name, material grade, pipe size range, PN rating, and date of manufacture | ☐ Yes ☐ No |  |

Part 3 - EHC-AF3-WS-TAZ-018-04 - Supply of Valves

| Item No 1 . Flang |  |  |  |
| --- | --- | --- | --- |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| A | Flanged Soft Sealing Gate Valves |  |  |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Design standard: EN 1074-1 & 2 | ☐ Yes ☐ No |  |
|  | - Face-to-face: EN 558 Table 2 Basic Series 3 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Flanges: EN1092-2 (ISO 7005-2), PN16 |  |  |
|  | - Body: Ductile Iron GJS-500-7 (GGG-50), FBE coating 250 µm |  |  |
|  | - Bonnet: Ductile Iron GJS-500-7 (GGG-50), FBE coating 250 µm |  |  |
|  | - Wedge core & body: Ductile Iron GJS-500-7 (GGG-50) |  |  |
|  | - Wedge shoe: Polyamide or equivalent |  |  |
|  | - Wedge rubber: EPDM, potable water approved |  |  |
|  | - Wiper ring & O-rings: NBR rubber |  |  |
|  | - Stem: Stainless Steel 316L |  |  |
|  | - Stem nut: Brass DZR CW626N |  |  |
|  | - Thrust collar: Brass DZR CW602N |  |  |
|  | - Stop ring: Stainless steel 316L |  |  |
|  | - Stem seal: EPDM rubber |  |  |
|  | - Bushing: Polyamide or equivalent |  |  |
|  | - Bonnet gasket: EPDM rubber |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304, sufficient for all flange faces |  |  |
| B | Flanged Metal Seated Gate Valves |  |  |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Design standard: EN 1074-1 & 2 | ☐ Yes ☐ No |  |
|  | - Face-to-face: EN 558 Table 2 Basic Series 3 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Body & gate: Ductile Iron GJS-500-7 (GGG-50), FBE coating 250 µm |  |  |
|  | - Body & gate seal ring: Bronze EN1982/BS CA104 or equivalent |  |  |
|  | - Stem & stem collar: Stainless Steel 316L |  |  |
|  | - Stem nut & bearing: Bronze EN1982/BS CA104 |  |  |
|  | - O-ring: EPDM rubber, potable water approved |  |  |
|  | - Cap top & support: Ductile Iron GJS-500-7 |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304, sufficient for all flange faces |  |  |
| 2 | Brass Threaded Gate Valve |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Design: Female/Female threaded, handle in steel | ☐ Yes ☐ No |  |
|  | - Body material: Brass CW617N or DZR CW602N |  |  |
|  | - Threads: ISO228 (DIN EN ISO 228 / BS EN ISO 228) |  |  |
|  | - Working temperature: 0°C to 90°C (no steam) |  |  |
| 3 | Flanged Check Valve (Swing/Non-return) |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Swing type | ☐ Yes ☐ No |  |
|  | - Standards: EN 558-1 Series 10, BS 5153 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Working temperature: up to 60°C |  |  |
|  | - Body & cover: Ductile Iron GJS-500-7 (GGG50), FBE coating 250 µm |  |  |
|  | - Seat: Bronze |  |  |
|  | - Sealing disc: Ductile Iron GJS-500-7 |  |  |
|  | - Shaft & lever shaft: Stainless Steel 316L or X20Cr13 |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304 |  |  |
| 4 | Flanged Double Orifice Air Relief Valve |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Flanged Double Orifice Air Relief Valve | ☐ Yes ☐ No |  |
|  | - Standard: EN 1074-4/BS 5153 (performance), EN 558-1 (dimensions) |  |  |
|  | - Body & bonnet: Ductile Iron GJS-500-7 (GGG50), FBE coating 250 µm |  |  |
|  | - Guides, orifice, seat, plug: ABS / PP / Polyamide |  |  |
|  | - Sealing ring & gasket: EPDM rubber |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Function: Triple Orifice (vent air during filling, admit air during draining, release entrained air) |  |  |
| 5 | Others for all Valves |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | The manufacturer shall operate under a certified Quality Management System compliant with ISO 9001:2015. | ☐ Yes ☐ No |  |
| 2 | Full material traceability certificates shall be provided upon request. | ☐ Yes ☐ No |  |
| 3 | Approved for contact with drinking water | ☐ Yes ☐ No |  |
| 4 | Valves shall be 100% factory tested to EN standards (shell, seat leakage, functional tests); type test reports for pressure, endurance, and coating will be submitted at delivery stage with all Factory Test Certificates | ☐ Yes ☐ No |  |
| 5 | Each valve shall be permanently and clearly marked with: | ☐ Yes ☐ No |  |
|  | Manufacturer’s name or trademark |  |  |
|  | ● Nominal diameter (DN) |  |  |
|  | ● Pressure rating (PN) |  |  |
|  | ● Material designation |  |  |
|  | ● Direction of flow (where applicable) |  |  |
| 6 | Packaging, Handling, and Transportation: | ☐ Yes ☐ No |  |
|  | Valves shall be individually protected against dust, moisture, and impact, with flange ends covered, and packaged suitably for long-distance transport and storage under harsh climatic conditions. |  |  |
|  | Warranty and Defect Liability: |  |  |
|  | The/supplier shall provide a minimum warranty of 12 months from date of handover certificate, during which any valve defective due to design, material, or manufacturing faults shall be repaired or replaced at no cost to the Purchaser. |  |  |

- Delivery requirements – Comparative Data Table:

| UNOPS Requirements |  | Is quotation compliant? Bidder to complete | Details Bidder to complete |
| --- | --- | --- | --- |
| Delivery time | The Bidder shall deliver the goods within 6 months after the Contract signature. | ☐ Yes ☐ No | Insert details |
| Delivery place and Incoterms rules | Part 1,2 and 3, DAP as per Incoterms 2020 at Warehouses of National/Local Water & Sanitation Authorities at Taiz City – Yemen | ☐ Yes ☐ No | Insert details |
| UNOPS Right to vary requirements | At the time the Contract is awarded, UNOPS reserves the right to vary the quantity of the goods and associated services specified above, provided this does not exceed +/- [20%] , without any change in the unit prices or other terms and conditions of the RFQ. | ☐ Yes ☐ No | Insert details |