Section II: Schedule of Requirements

Supply, testing, delivery and unloading of HDPE Pipes, DI Pipes, GI pipes and fittings to LWSCs- Warehouses of - Local Water and Sanitation Corporations/Authorities - Taiz (Al - Turbah) - Yemen

Lot 3:  Supply, testing, delivery and unloading of HDPE Pipes, DI Pipes, GI pipes and fittings to LWSCs- Warehouses of - Local Water and Sanitation Corporations/Authorities - Taiz (Al-Turbah) - Yemen

- Summary of requirements

| Part | Subproject ID | Description | Destination City |
| --- | --- | --- | --- |
| 1 | EHC-AF3-WS-TAZ-024-01 | Supply of HDPE Pipes and Fittings | Taiz (Al-Turbah) |
| 2 | EHC-AF3-WS-TAZ-024-02 | Supply of DI Pipes and Fittings | Taiz (Al-Turbah) |
| 3 | EHC-AF3-WS-TAZ-024-03 | Supply of Medium Class GI Pipes and Fittings | Taiz (Al-Turbah) |
| 4 | EHC-AF3-WS-TAZ-024-04 | Supply of Repair Clamps | Taiz (Al-Turbah) |
| 5 | EHC-AF3-WS-TAZ-024-05 | Supply of Valves | Taiz (Al-Turbah) |

## Technical specifications for Goods and Comparative Data Table

Part 1 - EHC-AF3-WS-TAZ-024-01 - Supply of HDPE Pipes and Fittings

| ITEM#1: HDPE Pipes: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1. 1 | Date of manufacture: New (2025) |  | ☐ Yes ☐ No |  |
| 1. 2 | Manufacturer/Brand |  | To be inserted by bidder |  |
| 1. 3 | Country of origin: |  | To be inserted by bidder |  |
| 1. 4 | Pressure Rating: | SDR 11 (PN16) | ☐ Yes ☐ No |  |
| 1.4.1 | Diameter Range | DN 25 mm – DN 110 mm, Please refer to additional Techn. Requirement | ☐ Yes ☐ No |  |
| 1. 5 | HDPE pressure Pipes | -100% virgin (with no recycled compound) PE. 100 | ☐ Yes ☐ No |  |  |
|  |  | -MRS ≥ 10 MPa |  |  |  |
|  |  | -Density 0.95–0.965 g/cm³ |  |  |  |
|  |  | -Physical Properties: Melt flow index 0.4–0.55 g/10min; tensile ≥ 25 N/mm²; elongation ≥ 600%; modulus 1200 N/mm² |  |  |  |
| 1. 6 | The standards for PE Pipes shall be Comply with current international standards or equivalents: |  | ☐ Yes ☐ No |  |  |
|  | ● DIN EN ISO 178 |  |  |  |  |
|  | ● DIN EN ISO 527-2 |  |  |  |  |
|  | ● DIN 7728-1 |  |  |  |  |
|  | ● DIN 8074 / ISO 4427 |  |  |  |  |
|  | ● DIN 8075 / ISO 4427 |  |  |  |  |
|  | ● DIN EN ISO 12162 |  |  |  |  |
|  | ● DIN 53752 |  |  |  |  |
|  | ● EN 12201 |  |  |  |  |
| 1. 7 | ● Use: Municipal and urban water supply and distribution systems. |  | ☐ Yes ☐ No |  |  |
|  | ● Compliance certificates verifying potable water suitability (WRAS, NSF, BS 6920, or equivalent). |  |  |  |  |
| 1. 8 | The bidder confirms that manufacturer quality-control test results and reports, as well as batch-traceability documents, will be provided at the delivery stage. |  | ☐ Yes ☐ No |  |  |
| 1. 9 | Packaging & Supply Format: Pipes with a nominal diameter of DN 110 mm or smaller shall be supplied in coiled form, with a maximum coil length of 100 meters , DN>110 mm straight |  | ☐ Yes ☐ No |  |  |
| 1. 10 | Certifications: Manufacturer shall hold valid ISO 9001, ISO 14001, OHSAS 18001 (or equivalent) certifications. |  | ☐ Yes ☐ No |  |  |
| 1.11 | Marking & traceability per ISO/DIN standards |  | ☐ Yes ☐ No |  |  |
| ITEM # 2: PP Compression Fittings (Couplings, Reducers, Tees, Adaptors, Elbows, End Caps) |  |  |  |  |  |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |  |
| 2. 1 | Date of manufacture | 2025 or newer | To be inserted by bidder |  |  |
| 2. 2 | Manufacturer |  | To be inserted by bidder |  |  |
| 2. 3 | Country of origin |  | To be inserted by bidder |  |  |
| 2. 4 | Pressure Rating: | PN16 (16 bar) | ☐ Yes ☐ No |  |  |
| 2. 5 | Types and SIZES | Please refer additional Techn. Requirement | ☐ Yes ☐ No |  |  |
| 2. 6 | - Material: PP-B (UV stabilized); EPDM seals; POM grip rings; stainless steel reinforcement |  | ☐ Yes ☐ No |  |  |
|  | - Pressure Class: PN16 (PN10 for some end caps) |  |  |  |  |
|  | - Threads BSP in accordance with ISO 7-1 / EN 10226 |  |  |  |  |
|  | - Standards: EN ISO 17885, EN 12201-3, EN 681-1or equivalent |  |  |  |  |
|  | - Potable water suitability certificates |  |  |  |  |
|  | - Marking & batch traceability |  |  |  |  |
| 2. 7 | Pressure Class: PN16 and PN10, please refer to additional Techn. Requirement |  | ☐ Yes ☐ No |  |  |
| 2. 8 | - Threads BSP in accordance with ISO 7-1 / EN 10226 |  | ☐ Yes ☐ No |  |  |
| 2. 9 | - Standards: EN ISO 17885, EN 12201-3, EN 681-1 or equivalent |  | ☐ Yes ☐ No |  |  |
| 2. 10 | - Potable water suitability certificates |  | ☐ Yes ☐ No |  |  |
| ITEM # 3: P.P. Mechanical Saddle with reinforcing metal ring: |  |  |  |  |  |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |  |
| 3. 1 | Date of manufacture | 2025 or newer | To be inserted by bidder |  |  |
| 3. 2 | - Manufacturer |  | To be inserted by bidder |  |  |
| 3. 3 | - Country of origin |  | To be inserted by bidder |  |  |
| 3. 4 | - Material: PP body, DI/metal rings ,EPDM gasket |  | ☐ Yes ☐ No |  |  |
|  | Pressure: PN10 or PN16 as , Please refer to additional Techn. Requirement |  |  |  |  |
|  | - Type. Mechanical Saddle with reinforcing metal ring |  |  |  |  |
|  | Sizes: Please refer to additional Techn. Requirement |  |  |  |  |
|  | - Standards: EN 12201, ISO 1167 or equivalent |  |  |  |  |
| ITEM # 4: Restraint Couplings & Flange Adaptors |  |  |  |  |  |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |  |
| 4.1 | - Date of manufacture | 2025 or above | ☐ Yes ☐ No |  |  |
| 4.2 | - Manufacturer |  | To be inserted by bidder |  |  |
| 4.3 | - Country of origin |  | To be inserted by bidder |  |  |
| 4.4 | - Standards: EN 12842 or equivalent |  | To be inserted by bidder |  |  |
|  | - Working Pressure:PN16 |  |  |  |  |
|  | - Flange Compatibility: EN1092-2or equivalent |  |  |  |  |
|  | - Angular Deflection: ≥ 1.5° |  |  |  |  |
|  | Sizes: Please refer to additional Techn. Requirement |  |  |  |  |
|  | Material: |  |  |  |  |
|  | - End Ring: Ductile Iron, FBE Coated |  |  |  |  |
|  | - Grip Ring: Copper Alloy |  |  |  |  |
|  | - Bolts :316 Stainless Steel with Delta Seal Coating |  |  |  |  |
|  | - Elastomeric Seals: EPDM |  |  |  |  |
|  | - Barrel: Ductile Iron, FBE Coated |  |  |  |  |
| Others |  |  |  |  |  |
| Item | UNOPS Min. Specifications required |  | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |  |
| 1 | Warranty: minimum 1-year against manufacturing defects, leakage, or premature failure from the handover certificate date |  | ☐ Yes ☐ No | Insert details |  |

Part 2 - EHC-AF3-WS-TAZ-024-02 - Supply of DI Pipes and Fittings

| Item No. 1 - Fittings |  |  |  |
| --- | --- | --- | --- |
| Item | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 2.1 | Date of manufacture: New (2025) | To be inserted by bidder |  |
| 2.2 | Manufacturer/Brand | To be inserted by bidder |  |
| 2.3 | Country of origin: | To be inserted by bidder |  |
| 2.4 | Classes: K12 (bends, equal tees, reducers/tapers, blanks); K14 (reducer tees) | ☐ Yes ☐ No |  |
| 2.5 | Connections: All double-flanged PN16 (EN 1092-2, or equivalent); complete with: | ☐ Yes ☐ No |  |  |
|  | - EPDM/NBR gaskets |  |  |  |
|  | - SS 304/316 or galvanized carbon steel bolts/nuts/washers |  |  |  |
| 2.6 | Types and sizes: Please refer to additional tech. requirement | ☐ Yes ☐ No |  |  |
| 2.7 | Material: Ductile iron pipes, spheroidal graphite cast iron (to ASTM A536 or equivalent); suitable for drinking water networks | ☐ Yes ☐ No |  |  |
| 2.8 | Standards: EN 545/ISO 2531 or equivalent | ☐ Yes ☐ No |  |  |
| 2.9 | Internal Lining: Cement mortar lining per ISO 4179 or equivalent, suitable for potable water | ☐ Yes ☐ No |  |  |
| 2.1 | External Coating: Zinc coating with protective finish per EN 545 / ISO 2531or equivalent. | ☐ Yes ☐ No |  |  |
| 2.11 | Testing & Inspection: | ☐ Yes ☐ No |  |  |
|  | - Factory hydrostatic tests |  |  |  |
|  | - Site Dimensional checks, coating/lining verification per EN 545 / ISO 2531 or equivalent. |  |  |  |
|  | - Compliance valid certificates Provided |  |  |  |
| 2.12 | Approvals & Compliance: Potable water compliance (WRAS, DVGW, ACS, KIWA, or equivalent) | ☐ Yes ☐ No |  |  |
| 2.13 | Marking & Traceability: Manufacturer/trademark, DN, class (K9/K12/K14), standard reference, batch/date | ☐ Yes ☐ No |  |  |
|  | Packaging & Delivery: Protective end caps, secure bundling, accessories in labelled containers; stored on timber supports, protected from contamination |  |  |  |
| 2.14 | Warranty: Minimum 12 months from handover certificate date against defects in materials, manufacture, or coatings/linings | ☐ Yes ☐ No |  |  |
| 2.15 | Documentation Requirements are provided: | ☐ Yes ☐ No |  |  |
|  | - Material test reports (chemical, mechanical properties) |  |  |  |
|  | - Hydrostatic test records |  |  |  |
|  | - Coating/lining inspection reports |  |  |  |
|  | - Potable water compliance certificates |  |  |  |

Part 3 - EHC-AF3-WS-TAZ-024-03 - Supply of Medium Class GI Pipes and Fittings

| (Medium Class) GI Pipes and Fittings |  |  |  |
| --- | --- | --- | --- |
| Item | Specifications required | Is quotation compliant? Bidder to complete | Bidder’s Offer specifications Bidder to complete |
| 1. GALVANIZED IRON (GI) PIPES |  |  |  |
| 1.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.2 | Manufacturer/Brand | To be inserted by bidder | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.3 | Country of origin: | To be inserted by bidder | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.4 | Pipes are suitable for cold potable water, for buried or exposed installation. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.5 | GI pipes comply with with BS 1387 or BS EN 10255 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.6 | Galvanizing Comply with BS 729 or ASTM A123 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.7 | Threads comply with with BS 21 / ISO 7-1 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.8 | Pipes manufactured from mild steel, uniform composition, defect-free | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.9 | Hot-dip galvanizing applied internally and externally after fabrication and threading | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.10 | Zinc coating mass ≥ 360 g/m² (Galvanizing test report is provided) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.11 | Galvanized surfaces shall be free from blisters, bare spots, peeling, or flaking. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.12 | Medium Class pipes as per BS 1387 / BS EN 10255 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.13 | Medium Series GI Pipes – Nominal Diameters and Minimum Wall Thickness: 20 mm (¾″) – 2.6 mm; 25 mm (1″) – 3.2 mm; 40 mm (1½″) – 3.2 mm; 50 mm (2″) – 3.6 mm; 80 mm (3″) – 4.0 mm. 100 mm (3″) – 4.5 mm | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.14 | Standard pipe length = 6.0 m | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.15 | Dimensional tolerances comply with 10255 or equivalent | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.16 | Pipes threaded at both ends | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.17 | One GI socket supplied per pipe | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.18 | Pipes suitable for working pressure ≥ 12 bar at at 20°C | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.19 | Pressure testing conducted at ≥ 1.5 × working pressure | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.20 | Pipes shall be permanently marked at intervals ≤ 1.5 m. - Marking shall include: - Manufacturer name - Nominal diameter (DN) - Wall thickness - Pipe class (Heavy) - Applicable standard - Batch number - Date of manufacture | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 1.21 | Minimum 12 months warranty from the handover certificate date. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2. GALVANIZED IRON (GI) FITTINGS |  |  |  |
| 2.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.2 | Manufacturer/Brand | To be inserted by bidder | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 23 | Country of origin: | To be inserted by bidder | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.4 | Fittings manufactured from malleable cast iron | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.5 | hot-dip galvanized Fittings | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.6 | Fittings shall comply with BS EN 10242 or equivalent. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.7 | All required fitting types and sizes are as per additional technical requirement (please refer to additional technical requirement) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.8 | Fittings pressure rating ≥ pipe pressure rating | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.9 | Galvanizing quality of fittings shall be equal to or better than pipes (manufacturer declaration required). | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.10 | Fittings are fully compatible with Medium Class GI pipes. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.11 | Visual inspection of galvanizing performed (Inspection report will be provided at delivery stage) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.12 | Coating adhesion verified by Preece Test (Test certificate will be provided at delivery stage) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.13 | Manufacturer operates documented QC system (ISO 9001 or equivalent is provided) | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.14 | Marking includes manufacturer, DN, standard reference | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |
| 2.15 | Minimum 12 months warranty from the handover certificate date. | ☐ Yes ☐ No | Insert details of goods offered, including specifications, picture, and brand/model offered if applicable |

Part 4 - EHC-AF3-WS-TAZ-024-04 - Supply of Repair Clamps

| Item No 1 - Stainless Steel Repair Clamp |  |  |  |
| --- | --- | --- | --- |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1.1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 1.2 | Manufacturer/Brand | To be inserted by bidder |  |
| 1.3 | Country of origin: | To be inserted by bidder |  |
| 1.4 | Clamp body material: Pre-rolled stainless steel 304L (or 316L for highly corrosive environments), fully welded, pickled, and passivated | ☐ Yes ☐ No |  |
| 1.5 | Clamp design: Integrated hinge point for simplified installation | ☐ Yes ☐ No |  |
| 1.6 | Fasteners: Stainless steel A4 bolts, nuts, washers, anti-galling treated | ☐ Yes ☐ No |  |
| 1.7 | Gasket: Waffle-structured EPDM rubber, vulcanized, rounded tops, fully circumferential | ☐ Yes ☐ No |  |
| 1.8 | Spanner plate: Vulcanized, integrated with gasket to maintain uniform compression | ☐ Yes ☐ No |  |
| 1.9 | Working pressure: - DN 80–150: 16 bar - DN 175–450: 10 bar; - DN 500+: 6 bar | ☐ Yes ☐ No |  |
| 1.1 | Tolerance (double band clamp): Max ±24 mm depending on pipe diameter | ☐ Yes ☐ No |  |
| 1.11 | Temperature range: -20°C to +80°C (standard EPDM) | ☐ Yes ☐ No |  |
| 1.12 | Corrosion resistance: Suitable for potable water | ☐ Yes ☐ No |  |
| 1.13 | Sealing: Fully circumferential with even compression to prevent leakage and minimize pipe stress | ☐ Yes ☐ No |  |
| 1.14 | Standards compliance: ISO 9001 (manufacturing) or equiv | ☐ Yes ☐ No |  |
| 1.15 | Installation: Quick and easy due to hinge design; even torque application ensures uniform gasket compression | ☐ Yes ☐ No |  |
| 1.16 | Warranty: Minimum 1-year against manufacturing defects and leakage | ☐ Yes ☐ No |  |
| 1.17 | Marking: Manufacturer name, material grade, pipe size range, PN rating, and date of manufacture | ☐ Yes ☐ No |  |

Part 5 - EHC-AF3-WS-TAZ-024-05 - Supply of Valves

| Item No 1 . Flanged Soft Sealing Gate Valves |  |  |  |
| --- | --- | --- | --- |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Design standard: EN 1074-1 & 2 | ☐ Yes ☐ No |  |
|  | - Face-to-face: EN 558 Table 2 Basic Series 3 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Flanges: EN1092-2 (ISO 7005-2), PN16 |  |  |
|  | - Body: Ductile Iron GJS-500-7 (GGG-50), FBE coating 250 µm |  |  |
|  | - Bonnet: Ductile Iron GJS-500-7 (GGG-50), FBE coating 250 µm |  |  |
|  | - Wedge core & body: Ductile Iron GJS-500-7 (GGG-50) |  |  |
|  | - Wedge shoe: Polyamide or equivalent |  |  |
|  | - Wedge rubber: EPDM, potable water approved |  |  |
|  | - Wiper ring & O-rings: NBR rubber |  |  |
|  | - Stem: Stainless Steel 316L |  |  |
|  | - Stem nut: Brass DZR CW626N |  |  |
|  | - Thrust collar: Brass DZR CW602N |  |  |
|  | - Stop ring: Stainless steel 316L |  |  |
|  | - Stem seal: EPDM rubber |  |  |
|  | - Bushing: Polyamide or equivalent |  |  |
|  | - Bonnet gasket: EPDM rubber |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304, sufficient for all flange faces |  |  |
| 2 | Brass Threaded Gate Valve |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Design: Female/Female threaded, handle in steel | ☐ Yes ☐ No |  |
|  | - Body material: Brass CW617N or DZR CW602N |  |  |
|  | - Threads: ISO228 (DIN EN ISO 228 / BS EN ISO 228) |  |  |
|  | - Working temperature: 0°C to 90°C (no steam) |  |  |
| 3 | Flanged Check Valve (Swing/Non-return) |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Swing type | ☐ Yes ☐ No |  |
|  | - Standards: EN 558-1 Series 10, BS 5153 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Working temperature: up to 60°C |  |  |
|  | - Body & cover: Ductile Iron GJS-500-7 (GGG50), FBE coating 250 µm |  |  |
|  | - Seat: Bronze |  |  |
|  | - Sealing disc: Ductile Iron GJS-500-7 |  |  |
|  | - Shaft & lever shaft: Stainless Steel 316L or X20Cr13 |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304 |  |  |
| 4 | Flanged Double Orifice Air Relief Valve |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | Date of manufacture: New (2025) | ☐ Yes ☐ No |  |
| 2 | Manufacturer/Brand | To be inserted by bidder |  |
| 3 | Country of origin: | To be inserted by bidder |  |
| 4 | Type/Model | To be inserted by bidder |  |
| 5 | - Flanged Double Orifice Air Relief Valve | ☐ Yes ☐ No |  |
|  | - Standard: EN 1074-4/BS 5153 (performance), EN 558-1 (dimensions) |  |  |
|  | - Body & bonnet: Ductile Iron GJS-500-7 (GGG50), FBE coating 250 µm |  |  |
|  | - Guides, orifice, seat, plug: ABS / PP / Polyamide |  |  |
|  | - Sealing ring & gasket: EPDM rubber |  |  |
|  | - Bolts, nuts, washers: Stainless Steel A2/304 |  |  |
|  | - Working pressure: PN16 |  |  |
|  | - Function: Triple Orifice (vent air during filling, admit air during draining, release entrained air) |  |  |
| 5 | Others for all Valves |  |  |
| Item No | UNOPS Min. Specifications required | Bidder to complete | Bidder to complete (Insert details of goods offered, including specifications, picture, and brand/model offered if applicable) |
| 1 | The manufacturer shall operate under a certified Quality Management System compliant with ISO 9001:2015. | ☐ Yes ☐ No |  |
| 2 | Full material traceability certificates shall be provided upon request. | ☐ Yes ☐ No |  |
| 3 | Approved for contact with drinking water | ☐ Yes ☐ No |  |
| 4 | Valves shall be 100% factory tested to EN standards (shell, seat leakage, functional tests); type test reports for pressure, endurance, and coating will be submitted at delivery stage with all Factory Test Certificates | ☐ Yes ☐ No |  |
| 5 | Each valve shall be permanently and clearly marked with: | ☐ Yes ☐ No |  |
|  | Manufacturer’s name or trademark |  |  |
|  | ● Nominal diameter (DN) |  |  |
|  | ● Pressure rating (PN) |  |  |
|  | ● Material designation |  |  |
|  | ● Direction of flow (where applicable) |  |  |
| 6 | Packaging, Handling, and Transportation: | ☐ Yes ☐ No |  |
|  | Valves shall be individually protected against dust, moisture, and impact, with flange ends covered, and packaged suitably for long-distance transport and storage under harsh climatic conditions. |  |  |
|  | Warranty and Defect Liability: |  |  |
|  | The/supplier shall provide a minimum warranty of 12 months from date of handover certificate, during which any valve defective due to design, material, or manufacturing faults shall be repaired or replaced at no cost to the Purchaser. |  |  |

- Delivery requirements – Comparative Data Table:

| UNOPS Requirements |  | Is quotation compliant? Bidder to complete | Details Bidder to complete |
| --- | --- | --- | --- |
| Delivery time | The Bidder shall deliver the goods within 6 months after the Contract signature. | ☐ Yes ☐ No | Insert details |
| Delivery place and Incoterms rules | Part 1,2,3,4 and 5, DAP as per Incoterms 2020 at Warehouses of National/Local Water & Sanitation Authorities at Taiz (Al - Turbah) - Yemen – Yemen | ☐ Yes ☐ No | Insert details |
| UNOPS Right to vary requirements | At the time the Contract is awarded, UNOPS reserves the right to vary the quantity of the goods and associated services specified above, provided this does not exceed +/- [20%] , without any change in the unit prices or other terms and conditions of the RFQ. | ☐ Yes ☐ No | Insert details |